- PURPOSE

To ensure the integrity of electrical appliances and the safety of personnel who use it.

- SCOPE

This procedure applies to all electrical equipment fitted with a 240 volt lead and plug used by GWMWater employees at office, depots or worksites.

- RESPONSIBILITIES

  - All Executive Managers:

- Ensure that the procedure is implemented and adhered to.

  - Facility Managers

Facility Managers shall arrange testing of all portable residual current devices in their respective departments in accordance with this procedure.

  - Manager Regional Operations:

(a)	Undertake an assessment of all electrical appliances which have a flexible cord including cord extension and electric portable outlet device (EPOD/Power Board) to identify the need and/or frequency of testing

- (b)	Ensure that the inspection process and recording is undertaken in line with agreed principals and practices.

  - All Staff:

- (a)	Use only approved and tested equipment

- (b)	Notify their Supervisor or Manager if equipment is substandard or damaged

- (c)	Ensure Register is updated when any new equipment is purchased

- (d)   The inspection and testing tasks shall be carried out by a competent person

- METHOD

  - Electrical Testing

- All Electrical equipment requiring testing will be tested in accordance with the AS/NZS 3760 and this procedure.

  - Frequency of Testing

- Testing will be carried out at frequencies of:

- Not required – fixed appliances and low voltage tools;

- 12 months – where there is a likelihood of wear, tear, abuse, flexing of the cord or the tool is used near water;

- 5 years – all other cases;

- Immediately – following natural disasters such as flood or fire is warranted / compromised due to inundation or heat etc.

  - Tagging Requirements

After the inspection and testing of portable electrical equipment the item must be fitted with an approved tag, the tagging must be done by a competent person and in accordance with AS/NZS 3012:2003. The name of the competent person who performed the test must be clearly and legibly marked on the tag.

  - Damaged or Non-compliant Equipment

Where general inspection or testing identifies equipment that is damaged or non-complying, it must be withdrawn from service immediately and records updated.

  - Purchased/Hired/Loaned Electrical Equipment

All electrical equipment hired/loaned by (or brought onto) the site must be inspected prior to hire/use and has been tested and tagged within 3 months prior to hiring/loaning. An inspection consists of a visual and tactile examination of the cord, plug and equipment to ensure their integrity, i.e. no cuts, breaks, burns or exposed wires.

  - Record keeping

Copies of the results of all inspections, tests and maintenance should be retained by the relevant tester and GWMWater.

- DOCUMENTATION

  - References

- AS/NZS 3760:2010 In-service safety inspection and testing of electrical equipment

  - Records

- Test & Tag Register

- DEFINITIONS

The reader is directed to the corporation’s standard definitions