- Purpose

The purpose of this Safe Work Instruction is to provide guidance and advice to management, supervisors, employees and contractors of GWMWater in relation to safety issues and the procedures that are to be followed when removing Meter or Stop Tap under Pressure on the Wimmera Mallee Pipeline.

- Scope

The scope of this Safe Work Instruction applies to All Water services Stop Taps and Meter assembly's on the Wimmera Mallee Pipeline

- Procedure

  - Arrive on site and determine problem with customer.

  - Check to see if water is still flowing through delivery side after Stop Tap is Shut Off, by Cracking Meter Nut.(Do not remove completely until no water is visible)

  - If no water is visible works may proceed on Meter after Stop tap.

  - If water is still under pressure it means Stop tap is not operating properly then water pressure needs to be stopped by 3 options below.

- Dig up Service line at copper inlet pipe until you find where it joins into poly pipe and apply a poly squasher to stop the water.

- Locate Ferrule at main and dig up and turn off.

- If service is on a small branch line turn on the scour outlet or install a hydrant.

  - Check pressure again at Meter nut and remove Meter if no water present.

  - Stop tap may now be removed and replaced if necessary.

  - Make sure new or repaired stop tap is in the off position.

  - Remove option of shutting down water and check water present at stop tap by turning on.

  - Reassemble Meter and check for leaks.

  - Leave stop tap in position found and try and contact customer to say job is completed.

## 3.1	General

  - Contact customer prior to determine problem.

  - Communications

- Mobile phone (in service) or equivalent on site

  - Fitness for task

- Persons must be fit for task

- Ensure that procedures for metallic water meter and pipe replacement as outlined in CMS 370 are followed

3.2	Equipment Required

- Fire Hydrant

- Poly Pipe Squasher

- Valve Shut off tool

- General Tools to Remove Meter or Stop Tap.

- Shovel to Expose Poly pipe.

- Legislation

OHS Act (Vic) 2004 s 21 (1), (2) a, c & e

- DEFINITIONS

The reader is directed to the corporation’s standard definitions.